| Company/Entity: Snowy Hydro Limited |
| --- |
| Main activity group (please check) |  | 1 | Generator user (owner) |
|  |  | 2 | Generator Manufacturer |
|  |  | 3 | Insurance Company, Reinsurance Company or Insurance Broker |
|  |  | 4 | Erection, Commissioning, Refurbishment, Maintenance. |
|  |  | 5 | Research Centers and Universities |
|  |  | 6 | Consulting Companies |
| Address: Monaro Highway Cooma NSW 2630 AUSTRALIA |
| Contact: Kapila Nanayakkara | e-mail: kapila.nanayakkara@snowyhydro.com.au |
| Telephone: +61 2 64 532722 | Fax: +61 2 64 532046 |
| This questionnaire has specific sections for each activity group. PLEASE CHOOSE THE ONE THAT YOU FIT MOST. The size of each specific section is reasonable. You can answer in a “skip if not applicable” basis, but we encourage you to participate in all sections where you feel comfortable to collaborate with this experience update, sharing your experience with the other groups. |
| Notes about the fulfillment of this questionnaire: You can fill the questionnaire directly in your computer – please use the check boxes and use the grey expandable fields that allow you to input your text information (therefore we did not number the pages) - and send the resulting file per e-mail – please rename it adding your name. It is also possible to print the questionnaire and fill it by hand, although this is a “computer version” (printed copies do not show the grey fields). In this case you can use the back of the pages for more space – don’t forget to indicate the corresponding answers items. In case of multiple answers / examples please feel free to send tables with the pertaining data. For our works’ sake we do prefer computer filled questionnaires Note of the Convener: Please feel free to contact Alexander Gromow should you need any assistance concerning this questionnaire – alexander.gromow@gifel.com.br . In fact we appreciate your questions in order to help to level the Questionnaires’ results. These additional questions themselves may be part of the experience update’s report. The validity of this Experience Update will rely on the quantity and quality of answers received therefore we are most interested in participate and collaborate with all the interested parties in order to gather these information and be able to elaborate a reliable conclusion report in the best possible way. |

1) Questionnaire with focus on Users of Hydro Generators (owners)

1.1) Are there standards recommending generator fire protection (GFP) in your country? - Yes - No

1.1.1) If yes, which standards are these? NA

1.2) Do you recommend or install generator fire protection? - Yes - No

1.2.1) What are the reasons for that? Risk of loss justifies the expenditure. (Each unit is assessed based on risk, likelihood of fire and consequence and cost of installing fire protection. Safety of personnel was an additional factor in underground power stations.)

1.3) Is there any difference between the present and past fire protection strategies on generators in your organisation? - Yes - No

1.3.1) If your organization changed the protection strategy, what are the reasons for the change? In the past we had CO2 protection on all our units. Moving from CO2 to water based protection on the basis of safety and effectiveness of existing CO2 systems. Now we are in the process of installing water based fire protection only on some generators based on risk analysis.

1.3.2) Do you intend to change the existing generator fire protection strategy in future and if so please give the reasons. Our existing strategy has been developed recently and in the process of implementation.

1.3.3) Do you have a single generator fire protection strategy to cover all the generators or do you have different strategies to cover different generators based on various factors? Please tick the relevant box: - Single strategy - Multiple strategies

1.3.3.1) If your organisation has multiple strategies to cover fire protection of different generators please tick and give brief explanation of the factors which contributed to use different strategies, as follows:

1.3.3.1.1) Generator Capacity (MVA) - Yes - No Brief explanation note: As this impacts on loss consequences- higher business impact.

1.3.3.1.2) Insulation Type (epoxy, polyester, bitumen etc) - Yes - No Brief explanation note: We do not consider that likelihood or consequences of fire greatly increased by type of ground insulation material

1.3.3.1.3) Insulation Temperature Class (Class B, Class F etc) - Yes - No Brief explanation note: We do not consider that likelihood of fire or consequences greatly increased by type of insulation temperature class or operating temperature

1.3.3.1.4) Location (remote, underground, surface etc) - Yes - No Brief explanation note: As this impacts on safety of personnel. We have decided to implement fire protection on two of our underground stations

1.3.3.1.5) Cooling media (air, windings water cooled, etc) - Yes - No Brief explanation note: All oor generators are air cooled.

1.3.3.1.6) Winding design features (roebel, multiturn, soft solder joints etc) -Yes -No Brief explanation note: as this impacts on greater likelihood of fires with multiturn and/or soft soldered strand joints

1.3.3.1.7) Generator Age - Yes - No Brief explanation note: We do not consider that likelihood of fire or consequences greatly increased by type of age as most of our generators falls into 30-50 year bracket.

1.3.3.1.8) Contamination (carbon dust, oil vapor etc) - Yes - No Brief explanation note: We do not consider that likelihood of fire or consequences greatly increased by contamination on our generators

1.3.3.1.9) Other factors - Yes - No Please specify these other factors and give a brief explanation note: Business consequences of Loss

1.4) Is there any requirement for the installation of generator fire protection made by a third party, for instance your insurance company or any authority having jurisdiction? - Yes - No

1.4.1) If yes, is there any specific generator fire protection type recommended? Please specify. NA

1.4.2) Is this a must or does it imply in reduction of insurance costs? - It is a must - No, in fact it implies in reduction of insurance costs Please comment: Not a direct impect on Premiums with or without gen fire protection, attention not to get confused by the redaction of this question, because there in no insurance cost reduction involved.

1.4.3) Is there a joint work between the technical department and the department responsible for the insurance of the plant (s) considering the cost reductions that may be achieved by reducing the risk by means of appropriate fire protection methods? - Yes - No Please comment if applicable: but no direct reduction in insurance premiums to justify fire protection

1.5) 1.5) Did you have fire in any of your generators in not least than the last 20 years? - Yes - No If yes, how many? One

1.5.1) Did they occur on the same type of generator? - Yes - No Please comment:

1.5.1.1) What was the reason for the fire to start? Please tick the relevant box indicating the trigger factor. If you have experienced more than one fire in not least than the last 20 years please copy the following table and fill it for each separate fire occurrence (please indicate the corresponding fire years).

1.5.1.1.1) Electrical Fault in the stator winding - Yes - No Additional information:

1.5.1.1.2) Electrical fault in the rotor winding - Yes - No Additional information:

1.5.1.1.3) Electrical fault in the exciter housing - Yes - No Additional information: Unit had CO2 generator fire suppression which did not cover the exciter housing directly. CO2 was not released and when fault was cleared fire went out.

1.5.1.1.4) Mechanical Fault in bearings - Yes - No Additional information:

1.5.1.1.5) Other Mechanical faults - Yes - No Additional information:

1.5.1.1.6) Any other? - Yes - No Additional information:

1.5.2) Please provide the following information on the units where fires occurred in not least than the last twenty years. If you have experienced more than one fire over the time your answer is covering, copy the following table and fill it for each separate fire occurrence (please specify the time span or the occurrence years).

1.5.2.1) Was the unit equipped with fire protection equipment? - Yes - No If Yes, what is the extinguishing media? (Eg. CO2, water, etc). If the media is chemical, please give the name. CO2

1.5.2.2) Did the fire protection system work according to the design specification? - Yes - No

1.5.2.3) Was the fire extinguished solely by the installed generator fire protection system without any additional external help? - Yes - No

1.5.2.4) Did the fire spread outside the generator? - Yes - No

1.5.2.5) Give a brief description of the damage to the generator and surrounding: exciter and brush holders damaged

1.5.2.6) Were there any direct or indirect fatalities as a result of the fire started in the generator? - Yes - No

1.5.2.7) Was the fire protection designed to trigger automatically in an event of a fire or/and heat detection? - Yes - No

1.6) Do you have different types of fire protection systems within the generators installed in your power plants? - Yes - No

1.6.1) If no, please indicate which is your sole fire protection system: - CO2 - Water Spray - Inergen - Other If other please indicate here which: CO2 has been removed and water based suppression is being installed on selected units. Water based fire suppression currently being installed on the following Hydro generators Tumut 1 generators (4x 82.4MW), Tumut 2 generators (4x 71.6MW). Planning to install water based fire suppression at Tumut 3 (6x 250MW), Murray 1 (10x 95MW), Murray 2 (4x 138MW) & Guthega (2x 30MW).

1.6.2) If yes, please indicate which are you’re the different fire protection systems you have installed: - CO2 - how many units? - Water Spray - how many units? - Inergen - how many units? - Other - how many units? If other please indicate here which:

1.6.3) In the case of CO2 please indicate the pressure system used: - High pressure - Low pressure Any comment on this issue?

1.6.4) Do you have generators with open circuit ventilation? - Yes - No If yes, which kind of fire protection, if any, do they have?

1.7) In your opinion/experience what is the most efficient fire extinguishing media? water

1.7.1) Which media is harmful to the machines?

1.7.2) Which media is harmful to the human health? CO2

1.7.3) Is there any environmental concern bound to any media currently in use? FM200

1.8) Do you specify measures to prevent accidents to personnel? - Yes - No If yes, please specify: isolation requirements and choice of Media

1.8.1) Do you specify measures to prevent damage to machine? - Yes - No If yes, please specify: two fire detections required before water released. (1-thermal and electric fault, and 2-smoke hi level and thermal)

1.9) By what means is the existing generator fire extinguishing system is designed to release? Automatically Manually or Either automatic or manual. If you have different fire protection systems please repeat the answer to each different fire protection system.

1.9.1) What is your opinion or preferred method, as to how the generator fire extinguishing system should be released? automatic as station are not manned

1.10) How is the fire detected in your generators? Please tick the box. - Heat - Smoke - Manual (By personnel) - Generator Electrical Protection relay operation plus one of above device operation - Any other; please specify:

1.10.1) Do you have any comment about the efficiency of these detectors (heat and/or smoke)? smoke is the most prone to false initiation. Need asperating system in generators due to high air flows. Use VESDA and require a high level of smoke to trip suppression and alarms at low levels of smoke.

1.11) How do you prevent unwanted (unnecessary-accidental) release of generator fire extinguishing system? (Eg- dual detection method) Please specify here: New water based fire suppression system will have two fire detections required before water released. (thermal and electric fault, and smoke hi level and thermal). Each generator will have eachs control board to reduce risk of multiple releases.

1.11.1) At your present installation did you have unwanted (unnecessary-accidental) release of generator fire extinguishing system with consequent release of extinguishing media? - Yes - No If yes, please specify: Number of unwanted (unnecessary-accidental) releases of fire protection per unit per year: In the past we had one per year CO2 releases- particularly where smoke was one of the inputs and release is managed by a central fire board. We have removed all CO2 installations and now in the process of installing water based protection on selected units. So far they have not mal-operated Outage duration that resulted due to clean up: 4hrs If you know the reason of these incidents, please specify? oil causing smoke

1.12) In an event of fire is detected by the devices installed (eg. Smoke, heat etc), will extinguishing media release immediately without any delay or any manual interference? - Yes - No If No, please inform the steps of releasing the extinguishing media:

1.13) Do you consider bearings as a potential fire hazard for generators? - Yes - No

1.13.1) Are your generator fire protection systems designed to fight bearing fires? - Yes - No - Do not know

1.14) Do you specify provisions to remove fire extinguishing media? - Yes - No If yes, for water –spray: does it include provisions for decontamination in case of water used for extinguishing a fire? Please specify here: drainage of water. Decontamination by station oil seperator. Minimise oil loss from bearings by placing thrower on shaft above bearings. If yes, for CO2: do you have an exhaust system that removes the media out of the room? Please specify here: For our removed CO2 system we didn't have exhaust system

1.15) Do you specify automatic open/close relief vents on the generator housing to relieve excessive inrush extinguishing media pressure while maintaining extinguishing media concentration within the generator housing for the specified extinguishing time? - Yes - No

1.16) What is the maximum number of machines protected by one storage? no maximum. size of supply to meet demand for one unit and manual fire fighting. redundancy to meet fire NFPA and Aust fire codes. Please specify the extinguishing media: water

1.16.1) Do you have main and reserve storage for each group of protected machines? - Yes - No If yes, please specify here:

1.17) What is the future trend for extinguishing media? water

1.18) What is the future trend for fire detection?

1.19) In case of fire, smoke constitutes a major problem on visibility, orientation, breathing capacity, etc. Therefore it is desirable to provide adequate means of combating while involving minimum risk to personnel. In this line please check which additional provisions you do foresee in your plants: - routine personnel fire fighting and fire escape training - clearly indicated (illuminated large numbers located low) escape routes - breathing apparatus (with pertinent use training) or air line system - emergency lightning located low and personnel own miner type hand lamps - areas subject to CO2 clearly indicated, with door interlocks, acoustic and visual alarms - use of odorized CO2 only with routine crew recognition training on the fragrance used - plant ventilation system tested not to recirculate smoke in to the housing in case of fire - routine check of the generator housing and proper maintenance of openings, doors, etc. - others, please specify: - all of the above - none of the above Comments on this issue:

1.19.1) Additionally to these items the existence on an Emergency Plan, a Fire Brigade and Simulations are very actual, being so please answer the following items: - yes, our company has an Emergency Plan for Catastrophic Situations - yes, our company has a trained Fire Brigade - yes, we do perform fire hazard situation simulations times a year. Comments on this issue:

1.20) Considering the existence of the recently launched standards (for instance NFPA 851), is there a need of any additional specific international standard on generator fire protection? - Yes - No Any additional comment? Please state here: We felt that it is a high level document and not descriptive enough to make decisions. Our fire protection decisions are based on risk (safety, finance, legal, environmental, community standing etc). We have to make decisions on a)whether to have a fire protection or not, b) if fir protection is needed should it be automatic or manual triggering, c) if automatic what should be the triggers, d) guide lines for selecting extinguishing materials etc.

1.21) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here:

2) Questionnaire with focus on Generator Manufacturers

2.1) From the generator manufacturer’s standpoint, do you recommend the use of Generator Fire Protection? - Yes - No

2.1.1) If yes, which type?

2.1.2) If not, please state your reasons.

2.2) From your experience, which is the type of generator fire extinguishing method more frequently used nowadays? - CO2 - Water Spray - Inergen - Other If other please specify:

2.2.1) Any change towards the former trend? - Yes - No If yes, please state it here:

2.3) Which Standards do you apply in the design of the fire protection of your generators?

2.3.1) Are there critical items in the application of these Standards that require special attention?

2.4) What is the state of the art in the detection in accordance to your experience? - smoke - heat - flame - other – please describe:

2.4.1) Which are the types of detection devices you normally use and/or recommend?

2.4.2) Do you recommend any specific detection and control system to minimize unwanted fire extinguishing system operation?

2.5) Does your company design generators suited to any of the existing fire extinguishing media (CO2, Water Spray, Halon substitutes, etc.), or there are limitations from your side? - No limitations - Yes, there are some limitations

2.5.1) Should you have limitations, please state them here:

2.6) From the fire protection standpoint, the generator and its housing have to be considered as a whole in the design when fire extinguishing is to be installed, in order to guarantee the system’s functionality and efficiency. Considering this fact are you always informed by the purchaser from the beginning of the generator’s design of the future application of a specific generator fire protection method? - Yes - No Any comments? Please state them here:

2.6.1) Are you requested to participate in the definition of the fire extinguishing system to be applied in one generator of your manufacture? - Yes - No Any comments? Please state them here:

2.6.2) Did you have to adapt a ready generator design to a specific fire extinguishing system? - Yes - No If yes, when: - before manufacture - during manufacture - after erection? Any comments? Please state them here:

2.7) Modern insulation materials are mostly considered to be non-flammable, fire retardant or self-extinguishable. Since these aspects are subject to test conditions that sometimes diverge from actual accident situations, please check how the insulation material you use can be classified: - flammable - non-flammable - fire retardant - self-extinguishable Any comments? Please state them here:

2.7.1) Do you test the flammability conditions of the materials you use by yourself? - Yes - No If not, who does these tests for you and under which conditions?

2.8) Has any of the hydro generators you manufactured suffered a fire accident? - Yes - No If yes, please state some details here:

2.8.1) Was the origin of the fire determined? - Yes - No If yes, please state some details here:

2.8.2) Was the generator equipped with fire protection system? - Yes - No If yes, please state which type here (CO2, water-spray, etc.):

2.8.2.1) Do you know if it did work properly? - Yes - No If yes, please state some details here:

2.8.3) Do you have any specific comment and/or information about the damages that occurred?

2.8.4) Would you like to state a general recommendation considering generator fire protection? - Yes - No If yes, please state it here:

2.9) Besides the design and production of new generators, does your company participate in the refurbishment and/or maintenance area? - Yes - No If yes, please state some details here:

2.9.1) If yes, does it include the fire extinguishing systems? - Yes - No If yes, please state some details here:

2.10) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here:

3) Questionnaire with focus on Insurance Companies, Reinsurance Companies or Insurance Brokers

3.1) Is fire protection for hydro generators required from a plant owner to insure a power plant? - Yes - No If yes, please state some details here:

3.1.1) Does the requirement of fire protection depend upon the size of the units or any other factors? - Yes - No If Yes, which are the factors you use to apply?

3.1.1.1) Do you require any kind of special supervisory technical equipment to be installed on the machines you cover the risk as for instance stator and runner temperature supervision/monitoring? - Yes - No If Yes, which are they, please comment?

3.1.2) Do you follow any standards or you have your own rules to deal with hydro generators? - Yes - No If yes, please state some details here:

3.1.2.1) What are the factors that imply in a reduction of hydro generators fire risks?

3.2) Does your company have preference for or recommends any one of the existing generator fire extinguishing methods? - Yes - No If yes, please specify here:

3.3) Is there a policy of insurance cost reduction depending upon the type of fire protection scheme the user installs? - Yes - No If yes, please specify here:

3.3.1) Is there any requirement from your side concerning maintenance of the fire fighting equipment and power plant’s personnel fire training? - Yes - No If yes , please specify here:

3.3.1.1) If you answered the last item (3.3.1) with yes do you verify if you customer is attending to the requirements of maintaining the equipment properly and keeping the personnel trained? - Yes - No If yes , please specify here:

3.4) Did you have any claim of refund of damages caused by isolated hydrogenerators fire in the last 30 years? - Yes - No

3.4.1) If yes, please give the basic available data (Plant, Country, Quantity of affected generators, year of the fire, etc). Should several examples be available please fell free to give the data in a table.

3.4.2) If yes, can you specify if the damaged plant had generator fire protection installed? - Yes - No

3.4.2.1) If yes, did fire protection work properly during the accident? - Yes - No Any additional comment and or information?

3.4.3) If yes, is it possible to inform the alleged cause of the fire? - electrical - mechanical - influence from outside the generator housing - other… Any additional comment and or information?

3.4.4) Was there any consequential damage to other units or to other equipment installed outside the generator housing? - Yes - No Any additional comment and or information?

3.4.4) Was the refund paid? - Yes - No If not, what were reasons that impeached the payment after your due diligence on the fire itself?

3.5) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here:

4) Questionnaire with focus on Erection, Commissioning, Refurbishment, Maintenance .

Please focus your answers depending upon your specialty: Erection, Commissioning, Refurbishment, or Maintenance and feel free to collaborate with answers to as many questions you deem to be able to contribute with your experience.

4.1) In your experience, have you dealt with hydro generators that were damaged by fire? - Yes - No If yes, please indicate the tasks you were involved with and list some basic machine data of the equipment itself:

4.1.1) Were the damaged generators equipped with fire a protection system? - Yes - No If yes, which type?

4.1.2) Did the fire protection system work? - Yes - No

4.1.2.1) According to your expertise, did its function help to reduce the extent of the damages caused by the fire? - Yes - No Any additional comment and or information?

4.1.3) Was the equipment recuperation cost covered by insurance? - Yes - No

4.1.3.1) Were you requested by the insurer to issue a report telling the real extend of the damages caused by the fire and/or by the extinguishing method used in the case? - Yes - No Any additional comment and or information?

4.2) According to your experience, do you recommend the use of generator fire protection? - Yes - No

4.2.1) If yes, which type? Why? water based but only where there is justified benefit of having fire protection eg Safety & economic benefit (risk reduction)

4.3) Taking into consideration your experience, do you have any general recommendations concerning hydro generator fire protection? - Yes - No If yes, please specify them here: Water based fire suppression where there is justified benefit. Manage generators with risk features such as soft soldered joints and multiturn windings. Even if fire suppresion not economic require regular stator resistance measurements and generator inspections

4.3.1) Do you have any specific comment for the hydro generator manufacturers regarding the generator fire protection? - Yes - No If yes, please state them here: not soft soldered joints and multiturn coils

4.3.2) Do you have any specific comment for the hydro generator users regarding the generator fire protection? - Yes - No If yes, please state them here:

4.4) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here:

5) Questionnaire with focus on Research Centers and Universities

The inclusion of this item has the aim of verify the real situation of materials used in modern hydro generators construction mainly focused on the flammability studies your institute may have made, either for manufactures (considering that many manufacturers closed their own laboratories due to rationalization aspects) or as a kind of “forensic” survey after some fire had occurred and the materials involved had to be checked either by initiative of users, manufactures or insurance companies. We would much appreciate to be granted wit your valuable cooperation on this subject.

5.1) Did you participate in any survey made specifically concerning the flammability of existing materials nowadays used in hydro generators manufacture? - Yes - No

5.1.1) If, yes, please describe the material, the survey purpose and briefly the test procedure.

5.1.2) Was the manufacturer’s initial specification confirmed by the test? - Yes - No

5.1.3) If not, can you comment which consequences this result had?

5.1.3.1) Was the material improved to meet the original requirements? - Yes - No

5.1.4) Did the test consider, as far as possible, the simulation of operational conditions (since some standards specify situations less stringent then those that do occur in the field)? - Yes - No If yes, please comment them here.

5.2) Did you participate in the development of new non flammable, fire-resistant or self-extinguishable materials to be used in hydro generators construction? - Yes - No

5.2.1) If yes, please describe the material and its purpose:

5.2.2) Is this new material already available at the market?

5.3) Your research is based upon which fire protection standards?

5.3.1) Do you participate in the development and actualization of fire protection standards? - Yes - No

5.3.2) If, yes, please state how.

5.4) Do you participate in the development and / or actualization of Generator Fire Protection Systems? - Yes - No

5.3.2) If, yes, please give a brief explanation. Here it is interesting to know the innovations achieved on the extinguishing processes – compared with the existing solution; including the fire detection and the resulting environmental improvements:

5.4) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here:

6) Questionnaire with focus on Consulting Companies.

This questionnaire is an update in which this particular section is dedicated to the Consulting Companies that usually issue at least the project specification for the Generator Fire Protection. As already stated before in our opinion from the fire protection standpoint, the generator and its housing have to be considered as a whole in the design when fire extinguishing is to be installed, in order to guarantee the system’s functionality and efficiency integrated in the concept of the power plant as a whole. With these questions we intend to get valuable information from the particular stand point of the Consulting Companies in order to compose a picture as complete as possible of the subject we are dealing with to see it the opinions do converge or not to the same point.

6.1) Is your company specialized in the design of the Generator Fire Protection: - Isolated (only the equipment itself) - Integrated in the power plant design - Whole power plant design including the Generator Fire Protection Any comment on that?

6.1.1) Should you work specifically with the Generator Fire Protection Equipment (not as a power plant designer) in which moment of the power plant’s project are you normally engaged by your customer: - bid stage (in order to get the data for the Generator Fire Detection’s specs) - after the generator supplier was already defined - in a stage when your expertise will be taken in to consideration in the whole project including the required civil work for the proper adaptation and safe function of the Generator Fire Protection - None of the above, please specify: Any comment on that?

6.2) There are the factors (or reasons) that lead your clients to order a Generator Fire Protection project from your company. According to your experience, considering these factors, who decides if the generators have to be equipped with Generator Fire Protection? - The customer that place the order to you (not necessarily the final user – it may be the integrator) - The insurance companies that demand it towards the final user in order to cover the power plant’s risk - The final user that may earn financial advantages towards the insurer by installing such a protection and requires it either directly or via integrator. - Power plant workers Labor Union Demands towards the final users - Final users’ own internal philosophy - You are asked to give an advice/opinion Any comment on that?

6.3) If the choice is yours do you have a preferred extinguishing method? - Yes - No If yes please indicate which: If no, please indicate how you determine the extinguishing media for each particular case:

6.3.1) – If you have the choice, which is the extinguishing media you usually chose for: a) Above water power plants (open-air): b) Cavern type power plants:

6.4) From your experience, which is the type of generator fire extinguishing method more frequently used nowadays? - CO2 - Water Spray - Inergen - Other If other please specify:

6.4.1) Do you recognize any change towards the former trend (status quo) in fire protection systems your country? - Yes - No If yes, please state it here:

6.5) Are there standards recommending generator fire protection in your country? - Yes - No

6.5.1) If yes, which standards are these?

6.5.2) If not which standards do you follow in your work?

6.5.2.1) Are there critical items in the application of these Standards that require special attention?

6.6) Considering the existence of the recently launched standards (for instance NFPA 851), is there a need of any additional specific international standard on generator fire protection? - Yes - No Any additional comment? Please state here:

6.5) What is the state of the art in the detection in accordance to your experience? - Smoke - Heat - Fame - Other – please describe:

6.5.1) Which are the types of detection devices you normally use and/or recommend?

6.5.2) Do you recommend any specific detection and control system to minimize unwanted fire extinguishing system operation (here is meant the unwanted release of the extinguishing media)?

6.6) Do you usually cooperate with the generator manufacturer on the Generating Fire Protection Question? - Yes, there is a cooperation and joint work - No, our work ends with the issue of the specifications - It depends from case to case, please specify:

6.7) Do you usually cooperate with fire protection equipment manufacturer on the Generating Fire Protection Question? - Yes, there is a cooperation and joint work - No, our work ends with the issue of the specifications - It depends from case to case, please specify:

6.8) Do you work also on refurbishment of Fire Protection Equipment on hydro generating plants? - Yes - No Do you have any comment on this issue you would share with us?

6.9) Do you follow you projects during erection and commissioning phrases? - Yes - No If yes, can you tell us what are the most frequent problems you had to face in the case of the Fire Protection Equipment?

6.10) In your opinion is a Generator Fire Protection installation required nowadays? - Yes - No Do you have any comment on this issue you would share with us?

6.11) According to your opinion, is there any question that is missing in this part of the questionnaire? - Yes - No If yes, please state it here: